## CNW-AD
SMARTEMP PRODUCT SELECTION CALCULATOR
Circular Nozzle [CNW-AD]
Inputs | [10 empty] | v 1.10 [08/2017]
Airflow Rate | 350 | [L/s] | [m3/h]
Maximum Permissible Pressure | 50 | Pa | default 50 Pa
Include Swirl Element [Type S1]
Results
| DN200 [S0] | DN250 [S0] | DN315 [S0] | DN400 [S0] | DN500 [S0] | DN630 [S0]
Throw (m) | 73.4877 | 57.3452 | 43.4738 | 30.9243 | 23.9525 | 17.5019
Sound Power Level (dB(A)) | 68.184 | 56.8635 | 44.8966 | 31.0837 | 21.879 | < 20
Total Pressure (Pa) | 889.0986 | 346.2604 | 133.7453 | 41.3223 | 19.6715 | < 10
Max Selected Total Pressure (Pa) | 50 | 50 | 50 | 50 | 50 | 50 | Key: | Suitable | Not Suitable | Warning
Min Centreline Distance (m) | 0.3 | 0.375 | 0.4725 | 0.6 | 0.75 | 0.945 | * | Refer to 'Notes CNW-AD' worksheet for notes and diffuser sizing
|  | click to see product on smartair.asia | [5 empty] | Copyright © 2016 SMARTAIR DIFFUSION
Group Box 19

## CNW-ADequations (hidden)
Units
Unit Selection | 1 | [L/s]
Unit Multiplier | 1
Airflow Rate
Input Values
Airflow Rate | 350
Pressure | 50
Swirl | FALSE
0
630 | Type 0 | [5 empty] | 500 | Type 0 |  |  |  | 400 | Type 0 |  |  |  | 315 | Type 0 |  |  |  | 250 | Type 0 |  |  |  | 200 | Type 0 |  |  |  | 400 | Type 1 |  |  |  | 315 | Type 1 |  |  |  | 250 | Type 1 |  |  |  | 200 | Type 1
Area | 0.089197 |  | 0.337 | m |  |  | Area | 0.060263 | 0.277 |  |  | Area | 0.041548 | 0.23 | m |  | Area | 0.023779 | 0.174 |  |  | Area | 0.014527 | 0.136 |  |  | Area | 0.0091609 | 0.108 |  |  | Area | 0.041548 | 0.23 |  |  | Area | 0.023779 | 0.174 |  |  | Area | 0.014527 | 0.136 |  |  | Area | 0.0091609 | 0.108
Velocity | 3.9239 | [5 empty] | Velocity | 5.8079 |  |  |  | Velocity | 8.4241 |  |  |  | Velocity | 14.719 |  |  |  | Velocity | 24.0935 |  |  |  | Velocity | 38.2059 |  |  |  | Velocity | 8.4241 |  |  |  | Velocity | 14.719 |  |  |  | Velocity | 24.0935 |  |  |  | Velocity | 38.2059
Throw (m) | 17.5019 |  |  | 6.178 | -6.74 |  | Throw (m) | 23.9525 |  | 5.078 | -5.54 | Throw (m) | 30.9243 |  | 4.217 | -4.6 | Throw (m) | 43.4738 |  | 3.19 | -3.48 | Throw (m) | 57.3452 |  | 2.493 | -2.72 | Throw (m) | 73.4877 |  | 1.98 | -2.16 | Throw (m) | 16.4044 |  | 2.0921 | -1.2194 | Throw (m) | 22.3362 |  | 1.5774 | -0.88224 | Throw (m) | 28.9387 |  | 1.2282 | -0.65343 | Throw (m) | 36.6093 |  | 0.9709 | -0.48483
SWL (dB(A)) | 12.173 |  |  | 29.095 | -125.54 |  | SWL (dB(A)) | 21.879 |  | 29.095 | -125.54 | SWL (dB(A)) | 31.0837 |  | 29.095 | -125.54 | SWL (dB(A)) | 44.8966 |  | 29.095 | -125.54 | SWL (dB(A)) | 56.8635 |  | 29.074 | -113.45 | SWL (dB(A)) | 68.184 |  | 28.789 | -100.46 | SPL (dB(A)) | 60.0798 |  | 27.323 | -93.553 | SPL (dB(A)) | 72.9038 |  | 27.323 | -93.553 | SPL (dB(A)) | 84.2284 |  | 27.323 | -93.553 | SPL (dB(A))
Total Pressure Loss (Pa) | 8.9991 |  | P-V | 50 | 825 |  | Total Pressure Loss (Pa) | 19.6715 | P-V | 50 | 558 | Total Pressure Loss (Pa) | 41.3223 | P-V | 50 | 385 | Total Pressure Loss (Pa) | 133.7453 | P-V | 50 | 214 | Total Pressure Loss (Pa) | 346.2604 | P-V | 50 | 133 | Total Pressure Loss (Pa) | 889.0986 | P-V | 50 | 83 | Total Pressure Loss (Pa) | 63.7603 |  |  |  | Total Pressure Loss (Pa) | 206.369 |  |  |  | Total Pressure Loss (Pa) | 534.2798 |  |  |  | Total Pressure Loss (Pa) | 1371.8791
Min Centreline Dist | 0.945 |  |  | 1.5 |  |  | Min Centreline Dist | 0.75 |  | 1.5 |  | Min Centreline Dist | 0.6 |  | 1.5 |  | Min Centreline Dist | 0.4725 |  | 1.5 |  | Min Centreline Dist | 0.375 |  | 1.5 |  | Min Centreline Dist | 0.3 |  | 1.5 |  | Min Centreline Dist | 0.8 |  | 2 |  | Min Centreline Dist | 0.63 |  | 2 |  | Min Centreline Dist | 0.5 |  | 2 |  | Min Centreline Dist | 0.4 |  | 2
| DN200 [S0] | DN250 [S0] | DN315 [S0] | DN400 [S0] | DN500 [S0] | DN630 [S0]
| DN250 [S1] | DN315 [S1] | DN400 [S1]
Results | DN200 [S0] | DN250 [S0] | DN315 [S0] | DN400 [S0] | DN500 [S0] | DN630 [S0]
Throw (m) | 73.4877 | 57.3452 | 43.4738 | 30.9243 | 23.9525 | 17.5019
SWL (dB(A)) | 68.184 | 56.8635 | 44.8966 | 31.0837 | 21.879 | 12.173
Total Pressure Loss (Pa) | 889.0986 | 346.2604 | 133.7453 | 41.3223 | 19.6715 | 8.9991
Permissible Pressure | 50 | 50 | 50 | 50 | 50 | 50
Min Centreline Dist | 0.3 | 0.375 | 0.4725 | 0.6 | 0.75 | 0.945
Results Validation | DN200 [S0] | DN250 [S0] | DN315 [S0] | DN400 [S0] | DN500 [S0] | DN630 [S0]
Throw (m) | 73.4877 | 57.3452 | 43.4738 | 30.9243 | 23.9525 | 17.5019
SWL (dB(A)) | 68.184 | 56.8635 | 44.8966 | 31.0837 | 21.879 | < 20
Total Pressure Loss (Pa) | 889.0986 | 346.2604 | 133.7453 | 41.3223 | 19.6715 | < 10
Permissible Pressure | 50 | 50 | 50 | 50 | 50 | 50
Min Centreline Dist | 0.3 | 0.375 | 0.4725 | 0.6 | 0.75 | 0.945

## Notes CNW-AD
SMARTEMP PRODUCT SELECTION CALCULATOR
Circular Nozzle [CNW-AD] Notes
Diffuser Sizing
Select Unit Size | DN400
|  | 1 | D3 | 398 | D3 = 398
|  | 2 | D1 | 230 | D1 = 230
|  | 3 | D2 | 467 | D2 = 467
|  | 4 | L | 194 | L = 194
|  | 5 | E | 24 | E = 24
|  | 6 | LE | 340 | Le = 340
ALL DIMENSIONS IN mm
Diffuser Location
Non Swirl Type Selected
|  | Size: DN200 [S0]; C ≥ 0.3 m | Size: DN250 [S0]; C ≥ 0.375 m | Size: DN315 [S0]; C ≥ 0.473 m | Size: DN400 [S0]; C ≥ 0.6 m | Size: DN500 [S0]; C ≥ 0.75 m | Size: DN630 [S0]; C ≥ 0.945 m
Size: DN200 [S0]; C ≥ 0.3 m
Size: DN250 [S0]; C ≥ 0.375 m
Size: DN315 [S0]; C ≥ 0.473 m
Size: DN400 [S0]; C ≥ 0.6 m
Size: DN500 [S0]; C ≥ 0.75 m
Size: DN630 [S0]; C ≥ 0.945 m
C
D3 = 398
D1 = 230
D2 = 467
L = 194
E = 24
Le = 340

## CNW-ADdata (hidden)
DN200
DN250
DN315
DN400
DN500
DN630
| DN200 | DN250 | DN315 | DN400 | DN500 | DN630
D3 | 198 | 248 | 313 | 398 | 498 | 620
D1 | 108 | 136 | 174 | 230 | 277 | 337
D2 | 257 | 302 | 384 | 467 | 600 | 733
L | 140 | 164 | 177 | 194 | 258 | 240
E | 20 | 24 | 24 | 24 | 28 | 32
Le | 340 | 340 | 340 | 340 | 415 | 450